SPECIFICATION PHRASES

GROUND-SOURCE PROBES

The probe pipe shall be made of high-pressure cross-linked polyethylene (PE-Xa) according to DIN 16892/16893, with a UV stabilised protective external PE coating

The probe(s) shall consist of a single continuous loop and there shall be no joint in the borehole

The probe shall be a double U-loop system, consisting of 2 single U-loop probes attached together

The probe tip will be covered in a GRP resin

The pipe shall have an life expectancy of 100 years at 20˚C and a maximum 15 bar operating pressure according to DIN 16892/16893

The pipe will have a Standard Dimension Ratio of 11 in a diameter of either 32 x 2.9mm or 40 x 3.7mm

The maximum and minimum operating temperatures of the probe shall be -40˚C to +95˚C

The pipe roughness shall be less than 0.007mm

The average thermal coefficient of longitudinal expansion of the pipe is 0.15mm/(m*K)

Connections to the probe shall be made using compression sleeve jointing technology

The probe shall have a 10 year manufacturer’s warranty

The probe shall be installed according to VDI Guideline 4640